## Sheet1
3 x 1 CC | [5 empty] | 1 x 1 CC
Net Capacity (MW) | Min 57% CTG | 75% CTG | Base No EC | Base + EC | Base + EC + WC | Net Capacity (MW) | Min 57% CTG | 75% CTG | Base No EC | Base + EC | Base + EC + DB | Base + EC + WC + DB
86°F, 70% RH | 1 | 2 | 3 | 4 | 5 | 86°F, 70% RH | 1 | 2 | 3 | 4 | 6 | 7
CT net ouput per CTG in CC | 42.1575 | 55.6088 | 74.291 | 76.7176 | 83.517 | CT net ouput per CTG in CC | 42.1575 | 55.6088 | 74.291 | 76.7176 | 83.517 | 83.517
ST net output - 3 x 1 CC | 102.6607 | 113.0419 | 136.284 | 138.1438 | 142.4832 | ST net output - 1 x 1 CC | 32.3146 | 35.7586 | 43.3058 | 43.9159 | 71.6057 | 71.5762
1x1 STCC | 63.969 | 80.461 | 106.621 | 109.664 | NA | 1 ea, 1x1 STCC | 71.162 | 87.949 | 113.972 | 116.985 | 143.858 | 150.586
2x1 DTCC | 142.088 | 175.888 | 228.819 | 234.924 | NA | 2 ea, 1x1 DTCC | 142.324 | 175.898 | 227.944 | 233.97 | 287.716 | 301.172
3x1 TTCC | 220.315 | 270.725 | 349.394 | 358.472 | 383.036 | 3 ea, 1 x1 TTCC | 213.486 | 263.847 | 341.916 | 350.955 | 431.574 | 451.758
1x1 STSC (Simple Cycle - Dump Cond) | 35.561 | 48.904 | 67.409 | 69.822 | NA | 1 ea, 1x1 STSC (Simple Cycle - Dump Cond) | 38.139 | 51.492 | 69.997 | 72.4 | NA | NA
2x1 DTSC (Simple Cycle - Dump Cond) | 76.711 | 103.416 | 140.427 | 145.242 | NA | 2 ea, 1x1 DTSC (Simple Cycle - Dump Cond) | 76.278 | 102.984 | 139.994 | 144.8 | NA | NA
3x1 TTSC (Simple Cycle - Dump Cond) | 117.87 | 157.929 | 213.444 | 220.663 | NA | 3 ea, 1x1 TTSC (Simple Cycle - Dump Cond) | 114.417 | 154.476 | 209.991 | 217.2 | NA | NA
Net Heat Rate (HHV, btu/kwh) | Min 57% CTG | 75% CTG | Base No EC | Base + EC | Base + EC + WC | Net Heat Rate (HHV, btu/kwh) | Min 57% CTG | 75% CTG | Base No EC | Base + EC | Base + EC + DB | Base + EC + WC + DB
86°F, 70% RH | 1 | 2 | 3 | 4 | 5 | 86°F, 70% RH | 1 | 2 | 3 | 4 | 6 | 7
CT net heat rate per CTG (HHV) in CC | 13516.864 | 11892.28 | 10931.144 | 10848.848 | 10744.2 | CT net heat rate per CTG (HHV) in CC | 13516.864 | 11892.28 | 10931.144 | 10848.848 | 10744.2 | 10744.2
1x1 STCC | 8908 | 8219 | 7617 | 7589 | NA | 1 ea, 1x1 STCC | 8008 | 7519 | 7126 | 7114 | 7455 | 7478
2x1 DTCC | 8021 | 7519 | 7098 | 7086 | NA | 2 ea, 1x1 DTCC | 8008 | 7519 | 7126 | 7114 | 7455 | 7478
3x1 TTCC | 7759 | 7328 | 6973 | 6965 | 7028 | 3 ea, 1 x1 TTCC | 8008 | 7519 | 7126 | 7114 | 7455 | 7478
1x1 STSC (Simple Cycle - Dump Cond) | 16024 | 13522 | 12048 | 11920 | NA | 1 ea, 1x1 STSC (Simple Cycle - Dump Cond) | 14941 | 12843 | 11602 | 11496 | NA | NA
2x1 DTSC (Simple Cycle - Dump Cond) | 14857 | 12789 | 11566 | 11461 | NA | 2 ea, 1x1 DTSC (Simple Cycle - Dump Cond) | 14941 | 12843 | 11602 | 11496 | NA | NA
3x1 TTSC (Simple Cycle - Dump Cond) | 14503 | 12562 | 11414 | 11315 | NA | 3 ea, 1x1 TTSC (Simple Cycle - Dump Cond) | 14941 | 12843 | 11602 | 11496 | NA | NA
Operation | Ramp Rate (MW/min) | Hot Start Time to MECL* (min) | Hot Start Time to Base No EC* (min) | Min Run Time (min) | Min Down Time (min) | Operation | Ramp Rate (MW/min) | Hot Start Time to MECL* (min) | Hot Start Time to Base No EC* (min) | Min Run Time (min) | Min Down Time (min)
CT (8.33 % of Base per min) | 7 | NA | NA | NA | NA | CT (8.33 % of Base per min) | 7 | NA | NA | NA | NA |  | Abbreviations
1x1 STCC | 13 | 12 | 42 | 60 | 30 | 1 ea, 1x1 STCC | 9 | 12 | 42 | 60 | 30 |  | CC = Combined Cycle
2x1 DTCC | 22 | 13 | 43 | 60 | 30 | 2 ea, 1x1 DTCC | 18 | 57 | 87 | 60 | 30 |  | CT = Combustion Turbine
3x1 TTCC | 35 | 14 | 44 | 60 | 30 | 3 ea, 1 x1 TTCC | 27 | 102 | 132 | 60 | 30 |  | CTG = Combustion Turbine Generator
1x1 STSC (Simple Cycle - Dump Cond) | 7 | 12 | 15 | 30 | 30 | 1 ea, 1x1 STSC (Simple Cycle - Dump Cond) | 7 | 12 | 15 | 30 | 30 |  | DB = Duct Burner
2x1 DTSC (Simple Cycle - Dump Cond) | 13 | 13 | 16 | 30 | 30 | 2 ea, 1x1 DTSC (Simple Cycle - Dump Cond) | 13 | 42 | 45 | 30 | 30 |  | DTCC = Dual Train combined cycle
3x1 TTSC (Simple Cycle - Dump Cond) | 20 | 14 | 17 | 30 | 30 | 3 ea, 1x1 TTSC (Simple Cycle - Dump Cond) | 20 | 72 | 75 | 30 | 30 |  | EC = Evaporative cooling
* with NFPA Purge Credit, hot steam lines, auxiliaries operating and one minute separation between CTG start commands. | [5 empty] | * with NFPA Purge Credit, hot steam lines, auxiliaries operating and 45 minute separation between CTG start commands for CC operation and 30 minutes between CTG start commands for simple cycle operation. | [6 empty] | EFOR = Equivalent Forced Outage Rate
HHV = High Heating Value
EFOR (%) | Year 1 | Year 2 | Year 3+ |  |  | EFOR (%) | Year 1 | Year 2 | Year 3+ |  |  |  | MECL = Minimum Environmental Compliance Load
CT | 3% | 2% | 1.5% |  |  | CT | 3% | 2% | 1.5% |  |  |  | NFPA = National Fire Protection Association
ST | 3% | 2% | 1.5% |  |  | ST | 3% | 2% | 1.5% |  |  |  | RH = Reheat
ST = Steam Turbine
STCC = Single Train combined cycle
TTSC = Triple Train Combined Cycle
SOURCE: NEXTERA | [12 empty] | WC = Wet Compression
total fuel consumption
inc heat rate |  | 5444.3308 | 5751.3323 | 6657.0961 | 7947.3835 | inc heat rate |  | 5446.0734 | 5797.792 | 6660.079 | 8939.4597 | 7969.7857
1x1 STCC | 569835.852 | 661308.959 | 812132.157 | 832240.096 | #VALUE! | 1 ea, 1x1 STCC | 569865.296 | 661288.531 | 812164.472 | 832231.29 | 1072461.39 | 1126082.108
2x1 DTCC | 1139687.848 | 1322501.872 | 1624157.262 | 1664671.464 | #VALUE! | 2 ea, 1x1 DTCC | 1139730.592 | 1322577.062 | 1624328.944 | 1664462.58 | 2144922.78 | 2252164.216
3x1 TTCC | 1709424.085 | 1983872.8 | 2436324.362 | 2496757.48 | 2691977.008 | 3 ea, 1 x1 TTCC | 1709595.888 | 1983865.593 | 2436493.416 | 2496693.87 | 3217384.17 | 3378246.324
1x1 STSC (Simple Cycle - Dump Cond) | 569829.464 | 661279.888 | 812143.632 | 832278.24 |  | 1 ea, 1x1 STSC (Simple Cycle - Dump Cond) | 569834.799 | 661311.756 | 812105.194 | 832310.4
2x1 DTSC (Simple Cycle - Dump Cond) | 1139695.327 | 1322587.224 | 1624178.682 | 1664618.562 |  | 2 ea, 1x1 DTSC (Simple Cycle - Dump Cond) | 1139669.598 | 1322623.512 | 1624210.388 | 1664620.8
3x1 TTSC (Simple Cycle - Dump Cond) | 1709468.61 | 1983904.098 | 2436249.816 | 2496801.845 |  | 3 ea, 1x1 TTSC (Simple Cycle - Dump Cond) | 1709504.397 | 1983935.268 | 2436315.582 | 2496931.2
extra fuel per CT | 569851.996 | 661192.913 | 812025.105 | 832431.368 |  | extra fuel per CT | 569865.296 | 661288.531 | 812164.472 | 832231.29 | 1072461.39
| 569736.237 | 661370.928 | 812167.1 | 832086.016 |  |  | 569865.296 | 661288.531 | 812164.472 | 832231.29 | 1072461.39
ST/CT | 0.81172 | 0.6776 | 0.61149 | 0.60023 | 0.56868 | ST/CT | 0.76652 | 0.64304 | 0.58292 | 0.57244 | 0.85738
ST power | 28.408 | 31.557 | 39.212 | 39.842 |  | ST power | 33.023 | 36.457 | 43.975 | 44.585
| 65.377 | 72.472 | 88.392 | 89.682 |  |  | 66.046 | 72.914 | 87.95 | 89.17
| 102.445 | 112.796 | 135.95 | 137.809 |  |  | 99.069 | 109.371 | 131.925 | 133.755