## technologies and projects
financial base year
2016
| Data from HSIS Appendix A, http://www.hnei.hawaii.edu/sites/www.hnei.hawaii.edu/files/Hawaii%20Solar%20Integration%20Study%20-%20Oahu.pdf | [7 empty] | min->2 | 2->3 | 3->4 | 4->max
| Note: horizontal block describes existing thermal technologies to add to database; vertical block describes existing projects to add (renewable techs are defined in new gen tech spreadsheet) |  |  |  | Power Points (MW) |  |  |  |  | Incremental Heat Rate (Btu/kWh) |  |  |  |  | Variable Cost |  | Outages | Fuel Consumption (MMBTU/hour)
[5 empty] | PP | PP | PP | PP | PP | IHR | IHR | IHR | IHR |  |  |  |  | FC | FC | FC | FC | FC
| technology | Plant | Fuel | Fuel Input @ Min Power (MMBtu) | Min | 2 | 3 | 4 | Max | 1 | 2 | 3 | 4 | Full Load Heat Rate (Btu/kWh) | Variable O&M ($/mwH) | Variable Cost ($/Hour) | FOR % | Min | 2 | 3 | 4 | Max | Full load heat rate (calculated) | Err
| Honolulu_8 | H8 | LSFO | 268.4 | 22.3 | 30.1 | 37.9 | 45.6 | 53.4 | 10579 | 10667 | 10755 | 10843 | 11265 | 0.32 |  | 15.1% | 268.4 | 350.9162 | 434.1188 | 516.9323 | 601.5077 | 11.2642 | -0.00081086
| Honolulu_9 | H9 | LSFO | 279.6 | 22.3 | 30.3 | 38.4 | 46.4 | 54.4 | 10080 | 10433 | 10785 | 11138 | 11400 | 0.32 |  | 15.1% | 279.6 | 360.24 | 444.7473 | 531.0273 | 620.1313 | 11.3995 | -0.00052757
| Waiau_3 | W3 | LSFO | 295.5 | 22.3 | 28.4 | 34.5 | 40.5 | 46.6 | 9115 | 10150 | 11185 | 12220 | 11904 | 0.32 |  | 15% | 295.5 | 351.1015 | 413.0165 | 480.1265 | 554.6685 | 11.9028 | -0.0012425
| Waiau_4 | W4 | LSFO | 272.3 | 22.3 | 28.4 | 34.5 | 40.5 | 46.6 | 10904 | 11292 | 11680 | 12068 | 11832 | 0.32 |  | 12% | 272.3 | 338.8144 | 407.6956 | 477.7756 | 551.3904 | 11.8324 | 0.00041202
| Waiau_5 | W5 | LSFO | 273.7 | 22.5 | 30.5 | 38.5 | 46.5 | 54.5 | 10364 | 10840 | 11316 | 11791 | 11526 | 0.32 |  | 4.7% | 273.7 | 356.612 | 443.332 | 533.86 | 628.188 | 11.5264 | 0.00038532
| Waiau_6 | W6 | LSFO | 276.2 | 22.5 | 30.3 | 38 | 45.8 | 53.5 | 10399 | 10893 | 11388 | 11882 | 11618 | 0.32 |  | 4.7% | 276.2 | 357.3122 | 441.1883 | 530.0147 | 621.5061 | 11.6169 | -0.0010636
| Waiau_7 | W7 | LSFO | 316 | 27 | 41 | 55 | 68.9 | 82.9 | 9247 | 9794 | 10340 | 10887 | 10600 | 0.32 |  | 5.2% | 316 | 445.458 | 582.574 | 726.3 | 878.718 | 10.5997 | -0.00026538
| Waiau_8 | W8 | LSFO | 314.1 | 27 | 41.8 | 56.6 | 71.3 | 86.1 | 8971 | 9358 | 9746 | 10133 | 10204 | 0.32 |  | 5.2% | 314.1 | 446.8708 | 585.3692 | 728.6354 | 878.6038 | 10.2045 | 0.00045761
| Waiau_9 | W9 | Diesel | 245.3 | 5.9 | 17.7 | 29.4 | 41.2 | 52.9 | 8514 | 9199 | 9883 | 10568 | 13115 | 3.3738 | 99.19 | 10.9% | 245.3 | 345.7652 | 453.3935 | 570.0129 | 693.6585 | 13.1126 | -0.0023629
| Waiau_10 | W10 | Diesel | 234.7 | 5.9 | 16.9 | 27.9 | 38.9 | 49.9 | 7904 | 8529 | 9155 | 9780 | 12499 | 3.5552 | 99.19 | 10.9% | 234.7 | 321.644 | 415.463 | 516.168 | 623.748 | 12.5 | 0.00095992
| Kahe_1 | K1 | LSFO | 387.9 | 36.5 | 47.9 | 59.3 | 70.7 | 82.1 | 9237 | 9531 | 9825 | 10118 | 10101 | 0.32 |  | 3.6% | 387.9 | 493.2018 | 601.8552 | 713.8602 | 829.2054 | 10.0999 | -0.001056
| Kahe_2 | K2 | LSFO | 383.4 | 36.7 | 48.1 | 59.4 | 70.8 | 82.1 | 9365 | 9444 | 9524 | 9603 | 9915 | 0.32 |  | 3.6% | 383.4 | 490.161 | 596.8782 | 705.4518 | 813.9657 | 9.9143 | -0.00067966
| Kahe_3 | K3 | LSFO | 373.9 | 36.3 | 48.8 | 61.2 | 73.7 | 86.1 | 9030 | 9188 | 9345 | 9502 | 9703 | 0.32 |  | 5.2% | 373.9 | 486.775 | 600.7062 | 717.5187 | 835.3435 | 9.702 | -0.0009849
| Kahe_4 | K4 | LSFO | 390.5 | 36.3 | 48.6 | 60.8 | 73.1 | 85.3 | 9041 | 9221 | 9402 | 9582 | 9927 | 0.32 |  | 5.2% | 390.5 | 501.7043 | 614.2005 | 729.8451 | 846.7455 | 9.9267 | -0.00032356
| Kahe_5 | K5 | LSFO | 569.7 | 54.7 | 74.6 | 94.5 | 114.4 | 134.3 | 9012 | 9133 | 9254 | 9375 | 9691 | 0.32 |  | 3.2% | 569.7 | 749.0388 | 930.7855 | 1114.9401 | 1301.5026 | 9.691 | 9.6798e-06
| Kahe_6 | K6 | LSFO | 579.7 | 54 | 74.1 | 94.2 | 114.3 | 134.4 | 9142 | 9450 | 9759 | 10067 | 10059 | 0.32 |  | 2.1% | 579.7 | 763.4542 | 953.3992 | 1149.5551 | 1351.9018 | 10.0588 | -0.00020685
| Kalaeloa_CC1 | Kal1 | LSFO | 637.3 | 67 | 72.8 | 78.5 | 84.3 | 90 | 5725 | 5832 | 5939 | 6047 | 8585 | 6 |  | 1.5% | 637.3 | 670.505 | 703.7474 | 738.1936 | 772.6615 | 8.5851 | 0.00012778
| Kalaeloa_CC2 | Kal2 | LSFO | 637.3 | 67 | 72.8 | 78.5 | 84.3 | 90 | 5725 | 5832 | 5939 | 6047 | 8585 | 6 |  | 1.5% | 637.3 | 670.505 | 703.7474 | 738.1936 | 772.6615 | 8.5851 | 0.00012778
| Kalaeloa_CC3 | Kal3 | LSFO | 0.1 | 0 | 28 |  |  |  | 8651 |  |  |  | 8654 | 6 |  | 1.5% | 0.1 | 242.328 | 242.328 | 242.328 | 242.328 | 8.6546 | 0.00057143
| AES | AES | Coal | 1284.7 | 67 | 96.5 | 126 | 155.5 | 185 | 15805 | 16106 | 16407 | 16708 | 17314 | 2 |  | 1.5% | 1284.7 | 1750.9475 | 2226.0745 | 2710.081 | 3202.967 | 17.3133 | -0.00066486
| H-Power | HPOWER | MSW | [11 empty] | 18 |  | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CIP_CT | CIP-CT1 | Biodiesel | 714.5 | 45 | 113 |  |  |  | 8915.3529 |  |  |  | 11688 | 40.76 |  | 15% | 714.5 | 1320.744 | 1320.744 | 1320.744 | 1320.744 | 11.688 | 0
| Airport_DSG | AiportDG | Biodiesel | 81.64 | 8 | [8 empty] | 10205 | 37.46 |  | 58% | 81.64 | 81.64 | 81.64 | 81.64 | 81.64 | 10.205 | 0
load_zone | technology | site | orientation | build_year | proj_existing_cap | proj_overnight_cost | proj_fixed_om | latitude | longitude | retirement year | unit_size | variable_o_m | forced_outage_rate | scheduled_outage_rate | fuel | heat_rate | intermittent | resource_limited | distributed | must_run | non_cycling | baseload | cogen
Oahu | Honolulu_8 | na | na | 1954 | 53.4 | 0 | 0 |  |  | 2016 | 53.4 | 0.32 | 0.151 | 0 | LSFO | 11265 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | Honolulu_9 | na | na | 1957 | 54.4 | 0 | 0 |  |  | 2016 | 54.4 | 0.32 | 0.151 | 0 | LSFO | 11400 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | Waiau_3 | na | na | 1947 | 46.6 | 0 | 0 |  |  | 2022 | 46.6 | 0.32 | 0.15 | 0 | LSFO | 11904 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | Waiau_4 | na | na | 1950 | 46.6 | 0 | 0 |  |  | 2022 | 46.6 | 0.32 | 0.12 | 0 | LSFO | 11832 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | Waiau_5 | na | na | 1959 | 54.5 | 0 | 0 |  |  | 2024 | 54.5 | 0.32 | 0.047 | 0 | LSFO | 11526 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | Waiau_6 | na | na | 1961 | 53.5 | 0 | 0 |  |  | 2024 | 53.5 | 0.32 | 0.047 | 0 | LSFO | 11618 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | Waiau_7 | na | na | 1966 | 82.9 | 0 | 0 |  |  | 2030 | 82.9 | 0.32 | 0.052 | 0 | LSFO | 10600 | 0 | 1 | 0 | 1 | 1 | 0 | 0
Oahu | Waiau_8 | na | na | 1968 | 86.1 | 0 | 0 |  |  | 2030 | 86.1 | 0.32 | 0.052 | 0 | LSFO | 10204 | 0 | 1 | 0 | 1 | 1 | 0 | 0
Oahu | Waiau_9 | na | na | 1973 | 52.9 | 0 | 0 |  |  | 2034 | 52.9 | 3.3738 | 0.109 | 0 | Diesel | 13115 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | Waiau_10 | na | na | 1973 | 49.9 | 0 | 0 |  |  | 2034 | 49.9 | 3.5552 | 0.109 | 0 | Diesel | 12499 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | Kahe_1 | na | na | 1963 | 82.1 | 0 | 0 |  |  | 2020 | 82.1 | 0.32 | 0.036 | 0 | LSFO | 10101 | 0 | 1 | 0 | 1 | 1 | 0 | 0
Oahu | Kahe_2 | na | na | 1964 | 82.1 | 0 | 0 |  |  | 2020 | 82.1 | 0.32 | 0.036 | 0 | LSFO | 9915 | 0 | 1 | 0 | 1 | 1 | 0 | 0
Oahu | Kahe_3 | na | na | 1970 | 86.1 | 0 | 0 |  |  | 2020 | 86.1 | 0.32 | 0.052 | 0 | LSFO | 9703 | 0 | 1 | 0 | 1 | 1 | 0 | 0
Oahu | Kahe_4 | na | na | 1972 | 85.3 | 0 | 0 |  |  | 2022 | 85.3 | 0.32 | 0.052 | 0 | LSFO | 9927 | 0 | 1 | 0 | 1 | 1 | 0 | 0
Oahu | Kahe_5 | na | na | 1974 | 134.3 | 0 | 0 |  |  | 2035 | 134.3 | 0.32 | 0.032 | 0 | LSFO | 9691 | 0 | 1 | 0 | 1 | 1 | 0 | 0
Oahu | Kahe_6 | na | na | 1981 | 134.4 | 0 | 0 |  |  | 2042 | 134.4 | 0.32 | 0.021 | 0 | LSFO | 10059 | 0 | 1 | 0 | 1 | 1 | 0 | 0
Oahu | Kalaeloa_CC1 | na | na | 1989 | 90 | 0 | 0 |  |  | 2050 | 90 | 6 | 0.015 | 0 | LSFO | 8585 | 0 | 1 | 0 | 1 | 1 | 0 | 0
Oahu | Kalaeloa_CC2 | na | na | 1991 | 90 | 0 | 0 |  |  | 2052 | 90 | 6 | 0.015 | 0 | LSFO | 8585 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | Kalaeloa_CC3 | na | na | 1991 | 28 | 0 | 0 |  |  | 2052 | 28 | 6 | 0.015 | 0 | LSFO | 8654 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | AES | na | na | 1992 | 185 | 0 | 0 |  |  | 2053 | 185 | 2 | 0.015 | 0 | Coal | 17314 | 0 | 1 | 0 | 1 | 1 | 0 | 0
Oahu | H-Power | na | na | 1989 | 73 | 0 | 0 |  |  | 2050 | 73 | 18 | 0.1 | 0.4137 | MSW | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1
Oahu | CIP_CT | na | na | 2009 | 113 | 0 | 0 |  |  | 2070 | 113 | 40.76 | 0.15 | 0 | Biodiesel | 11688 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | Airport_DSG | na | na | 2013 | 8 | 0 | 0 |  |  | 2074 | 8 | 37.46 | 0.58 | 0 | Biodiesel | 10205 | 0 | 1 | 0 | 0 | 0 | 0 | 0
Oahu | DistPV |  |  | 2016 | 444 | 0 | 0
Oahu | CentralTrackingPV |  |  | 2012 | 5 | 0 | 0 | 21.32 | -158.0869
Oahu | CentralTrackingPV |  |  | 2016 | 27.6 | 0 | 0 | 21.4619 | -158.1893
Oahu | OnshoreWind |  |  | 2011 | 30 | 0 | 0 | 21.682 | -157.976
Oahu | OnshoreWind |  |  | 2012 | 69 | 0 | 0 | 21.62 | -158.048
note: project build data will get stored in one built_project table,but scenario_data.py will extract it into proj_existing_builds.tab and proj_build_costs.tab
Notes:
Honua was removed because the company behind it went bankrupt in Feb. 2016 without completing the project. see:
Star-Advertiser "Pulling the Plug", 2016-02-08, http://www.pressreader.com/usa/honolulu-star-advertiser/20160208/281848642645296
http://www.ct-si.org/events/APCE2011/sld/pdf/9.pdf
http://oeqc.doh.hawaii.gov/Shared%20Documents/EA_and_EIS_Online_Library/Oahu/2010s/2010-04-08-OA-FEA-Honua-Power.pdf
TODO:
report reserves provided by each source
jdfvbkmnjjjuhjuhnbvcxzp,lmpn/////[
.,?"P}o?P<K?"<K?"op]k?"PKOP']/K<"}¦OPKPO"}<K?"KL,l?"LK?"K<">K?">L
TODO later:
add code to support non_cycling flag in switch unit commitment
limit Airport DSG to 1500 hours/year
add Tesoro cogen plant (built in 1983; assume 61-year life)
add Chevron cogen plant (G1-G3 built in 1990, G4 built in 2011; assume 61-year life)
fill in capital costs for all plants (use original cost, converted to 2016$; this reflects the fact that payments escalate with inflation in switch)
get better fixed and variable O&M for all plants
In Ulupono scenarios, switch wind and solar to 35-year life to avoid retirement and replacement by 2045
include pumped storage in reserve requirements and provision
allow specification of O&M per hour (based on commitment), rather than just per MWh (based on dispatch)
create flag for cost-only projects (not committed/dispatched, just built/retired)
convert batteries, hydrogen, evs? and fuel market expansion into projects with side constraints imposed by modules
define multiple speeds of regulating reserve product, with separate targets at each speed (to account for renewable mis-forecast)
(we don't define a contingency reserve product for extreme misforecasts, because it is hard to bound the quantity, and it can be a slow-start product (not instant-start), and most likely it would be addressed by rolling blackouts, not dipping into n-1 reserves)
allow users to specify a "greenfield" model, omitting all previous builds (in scenario_data.py)
Note on P16: converted hourly cost to cost per MWh, assuming operation in middle of range
Note on P17: converted hourly cost to cost per MWh, assuming operation in middle of range
Note on P24: From p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on P27: From p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on E28: Removed heat rate (74014!) because it runs on waste, which is a non-fuel in SWITCH-Hawaii.
Note on G28: removed 73 MW operating point because we don't use a heat rate curve for MSW (treat as non-fuel energy source)
Note on P28: From p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on C29: This is Siemens SGT6-3000E per final order in docket 2005-0145
Note on K29: Assigned a value to make consistent with full-load heat rate
Note on E30: Changed from 40.8 to be consistent with 8 MW min/max load and 10,205 full load heat rate
Note on F30: Changed from 0 because HECO can only run gen at 8 MW (and only 1500 h/y) per application (p. 23) in docket 2008-0329
Note on K30: removed 10,205 from here because it has no corresponding power point
Note on E33: from EIA 860 or 923 database unless otherwise noted
Note on G33: $/kW
Note on H33: $/kW-year
Note on K33: from 2016-04-01 PSIP, Book 2, pp. 93-95 (Theme 2) unless otherwise noted
Note on Q33: full load heat rate, Btu/kWh
Note on U33: closest match to HECO's definition of "baseload" -- must be committed, but level can be adjusted. from Hawaii RPS Study, GE Energy Management Energy Consulting. 8.2 Thermal Generating Characteristics, Table 7: Thermal Generating Unit Properties
Note on V33: Must be fully committed or fully non-committed during each timeseries (day)
Note on K42: set to 61 years, based on average age of already-scheduled retirements
Note on K43: set to 61 years, based on average age of already-scheduled retirements
Note on K48: set to 61 years, based on average age of already-scheduled retirements
Note on K49: set to 61 years, based on average age of already-scheduled retirements
Note on K50: set to 61 years, based on average age of already-scheduled retirements
Note on K51: set to 61 years, based on average age of already-scheduled retirements
Note on K52: set to 61 years, based on average age of already-scheduled retirements
Note on K53: set to 61 years, based on average age of already-scheduled retirements
Note on B54: note: nameplate capacity is 97.3 MW and winter/summer capacity are 86.0 MW per EIA form 860M for September 2016
Note on F54: note: nameplate capacity is 97.3 MW and winter/summer capacity are 86.0 MW per EIA form 860M for September 2016
Note on K54: set to 61 years, based on average age of already-scheduled retirements
Note on O54: 42.8 MW baseload operation per monthly and annual avg production in EIA form 923 for 2015
Note on K55: set to 61 years, based on average age of already-scheduled retirements
Note on B56: "Airport Dispatchable Standby Generation" (docket 2008-0329)
Note on E56: planned for late 2013 according to https://puc.hawaii.gov/wp-content/uploads/2015/04/Adequacy-of-Supply-HECO-2013.pdf
Note on K56: set to 61 years, based on average age of already-scheduled retirements
Note on C57: site and orientation for existing renewable projects will be looked up in import_data.py
Note on D57: site and orientation for existing renewable projects will be looked up in import_data.py
Note on F57: 444 MW DistPV installed by 2016 according to PSIP 2016-04-01 Figure J-19
Note on B58: Kalaeloa Solar 2 (5 MW PV) (KAS1 was canceled) should be CentralFixedPV, but we don't generally activate that, so this will do
Note on C58: site and orientation for existing renewable projects will be looked up in import_data.py
Note on D58: site and orientation for existing renewable projects will be looked up in import_data.py
Note on I58: location from EIA form 860M database (September 2016)
Note on B59: Waianae Solar (Eurus) from PSIP 2016-04-01; matched to specific project with query below
Note on C59: site and orientation for existing renewable projects will be looked up in import_data.py
Note on D59: site and orientation for existing renewable projects will be looked up in import_data.py
Note on I59: Mauka of Kamaile academy according to http://eurusenergy.com/news/press-releases/eurus-energy-america/waianae-solar-project-construction-financing/
Note on B60: Kahuku wind farm
Note on C60: site and orientation for existing renewable projects will be looked up in import_data.py
Note on D60: site and orientation for existing renewable projects will be looked up in import_data.py
Note on I60: found via Google Maps search
Note on B61: Kawailoa Wind Farm
Note on C61: site and orientation for existing renewable projects will be looked up in import_data.py
Note on D61: site and orientation for existing renewable projects will be looked up in import_data.py
Note on I61: found via Google Maps search
Note on A100: 444 MW DistPV installed by 2016 according to PSIP 2016-04-01 Figure J-19