## info
|  |  |  | o&m cost base year | 2016
technology | min_vintage_year | unit_size | connect_cost_per_kw_generic | fixed_o_m_per_kw_year | variable_o_m_per_mwh | fuel | full_load_heat_rate | max_age_years | forced_outage_rate | scheduled_outage_rate | intermittent | resource_limited | distributed
OnshoreWind | 2016 | NA | 456.6667 | 27.4 | 0 | WND | 0 | 25 | 0 | 0 | 1 | 1 | 0
OffshoreWind | 2025 | NA | 0 | 96.71 | 0 | WND | 0 | 25 | 0 | 0 | 1 | 1 | 0
CentralFixedPV | 2016 | NA | 415 | 22.97 | 0 | SUN | 0 | 25 | 0 | 0 | 1 | 1 | 0
CentralTrackingPV | 2016 | NA | 415 | 22.97 | 0 | SUN | 0 | 25 | 0 | 0 | 1 | 1 | 0
DistPV | 2016 | NA | 0 | 0 | 0 | SUN | 0 | 25 | 0 | 0 | 1 | 1 | 1
CC_152 | 2016 | 152 | 153.2895 | 17.29 | 4.49 | LSFO | 7114 | 30 | 1.6% | 5% | 0 | 0 | 0
CC_383 | 2016 | 383 | 79.3734 | 17.29 | 4.49 | LSFO | 6965 | 30 | 1.6% | 5% | 0 | 0 | 0
CT_100 | 2016 | 100 | 162 | 9.01 | 12.99 | LSFO | 10849 | 30 | 1.6% | 5% | 0 | 0 | 0
IC_Barge | 2016 | 100 | 162 | 34.46 | 20.96 | LSFO | 8507 | 30 | 2% | 2% | 0 | 0 | 0
IC_Schofield | 2016 | 54 | 279.6296 | 34.46 | 20.96 | LSFO | 8894 | 30 | 2% | 2% | 0 | 0 | 0
IC_MCBH | 2016 | 27 | 507.4074 | 34.46 | 20.96 | LSFO | 8575 | 30 | 2% | 2% | 0 | 0 | 0
Note on C3: Use NA for small, modular technologies
Note on H3: These are scattered through PSIP, but also reported in detail in "PSIP 2016 New Resource Assumptions.xlsx" from HECO.
Note on I3: assumed 25 for renewables because projects tend to be kept running a long time on Oahu. Assumed 30 years for thermal plants, per e-mail from Todd Kanja at HECO 2016-05-05 (he said this is their assumption for PSIP).
Note on J4: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on B5: per discussion with Ulupono 5/3/16
Note on J5: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on J6: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on J7: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on J8: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on J9: From PSIP p. D-28
Note on K9: From PSIP p. D-28
Note on H10: From 2016-04-01 PSIP, p. D-29
Note on J10: From PSIP p. D-28
Note on K10: From PSIP p. D-28
Note on H11: Assumed same as for CC 152 and CC 383 operating in CT-only mode (in HECO New Resource Assumptions spreadsheet).
Note on J11: From PSIP p. D-28
Note on K11: From PSIP p. D-28
Note on H12: PSIP p. D-42
Note on J12: From HECO New Resource Assumptions spreadsheet
Note on K12: From HECO New Resource Assumptions spreadsheet
Note on H13: From HSIS Appendix A?
Note on J13: From HECO New Resource Assumptions spreadsheet
Note on K13: From HECO New Resource Assumptions spreadsheet
Note on J14: From HECO New Resource Assumptions spreadsheet
Note on K14: From HECO New Resource Assumptions spreadsheet

## costs
copied from "PSIP 2016 New Resource Assumptions UPDATED 11-MAR-16.xlsx" with state tax credit omitted from renewables
these are nominal project costs; also shown in PSIP J-67 - J-70 and Appendix F
short names assigned manually below
inflation rate | 1.8%
Technology ID | OnshoreWind | OffshoreWind | MauiOahuWind200 | MauiOahuWind400 | CentralFixedPV | DistPV | SolarCSPStorage | CC_383 | CC_152 | CT_100 | Biomass | IC_MCBH | IC_Schofield | IC_Barge | CentralTrackingPV
Technology | On-Shore Wind | Offshore Wind Floating Platform | On Shore Wind + Cable | On Shore Wind + Cable | Utility Scale Solar PV | DG Solar PV | Solar CSP w 10 hrs storage | Combined Cycle Gas | Combined Cycle Gas | Simple Cycle Gas | Biomass | Internal Combustion | Internal Combustion | Internal Combustion | Utility Scale Tracking Solar PV
Primary Data Source | IHS Energy RS Means | NREL | IHS Energy RSMeans Vendor Quotes | IHS Energy RSMeans Vendor Quotes | IHS Energy RSMeans | IHS Energy RSMeans | NREL | NextEra | NextEra | Gas Turbine World RSMeans | NREL | HECO | HECO Schofield Application | HECO | IHS Energy RSMeans (adjusted)
Size (MW) | 30 | 400 | 200 | 400 | 20 | DG-PV | 100 | 383 (3 x 1) | 152 (1 x 1) | 100 | 20 | 27 (3 x 9 MW) | 54 (6 x 9 MW) | 100 (6 x 16.8 MW) Power Barge | 20
Fuel | NA | NA | NA | NA | NA | NA | NA | Gas / Oil | Gas / Oil | Gas / Oil | Biomass | Gas / Oil | Gas/Oil | Gas / Oil | NA
Hawaii Specific Nominal (As-Spent) Overnight Capital Cost $/KWAC (AFUDC NOT included)
Island | Oahu | Oahu | Maui --> Oahu | Maui --> Oahu | Oahu | Oahu | Oahu | Oahu | Oahu | Oahu | Oahu / Maui / Hawaii | Oahu / Maui / Hawaii | Oahu/ Maui/ Hawaii | Oahu | Oahu
Install Year
2016 | 2465 | 5062 | N/A | N/A | 2793 | 3945 | 12304 | 1758 | 1660 | 1237 | 6296 | 3177 | 2493 | 1323 | 3091.851
2017 | 2504 | 4849 | N/A | N/A | 2627 | 3716 | 12525 | 1783 | 1683 | 1253 | 6092 | 3219 | 2526 | 1347 | 2908.089
2018 | 2443 | 4626 | N/A | N/A | 2547 | 3573 | 11681 | 1797 | 1697 | 1261 | 6178 | 3238 | 2541 | 1371 | 2819.529
2019 | 2428 | 4565 | N/A | N/A | 2484 | 3457 | 10781 | 1822 | 1720 | 1277 | 6269 | 3280 | 2574 | 1396 | 2749.788
2020 | 2480 | 4500 | 5097 | 4572 | 2432 | 3360 | 9848 | 1845 | 1742 | 1292 | 6354 | 3319 | 2604 | 1421 | 2692.224
2021 | 2520 | 4431 | 5207 | 4672 | 2392 | 3285 | 8874 | 1870 | 1766 | 1309 | 6446 | 3362 | 2638 | 1447 | 2647.944
2022 | 2586 | 4358 | 5324 | 4778 | 2357 | 3218 | 7867 | 1896 | 1790 | 1326 | 6541 | 3406 | 2672 | 1473 | 2609.199
2023 | 2644 | 4249 | 5456 | 4899 | 2328 | 3160 | 7813 | 1921 | 1813 | 1342 | 6633 | 3448 | 2705 | 1499 | 2577.096
2024 | 2691 | 4134 | 5560 | 4992 | 2304 | 3111 | 7756 | 1944 | 1836 | 1358 | 6725 | 3487 | 2736 | 1526 | 2550.528
2025 | 2722 | 4013 | 5664 | 5085 | 2284 | 3068 | 7694 | 1969 | 1859 | 1373 | 6826 | 3527 | 2768 | 1554 | 2528.388
2026 | 2753 | 4026 | 5758 | 5166 | 2270 | 3034 | 7627 | 1992 | 1881 | 1388 | 6918 | 3564 | 2797 | 1582 | 2512.89
2027 | 2773 | 4037 | 5851 | 5248 | 2257 | 3004 | 7555 | 2021 | 1909 | 1408 | 7019 | 3617 | 2838 | 1610 | 2498.499
2028 | 2805 | 4048 | 5948 | 5333 | 2247 | 2976 | 7478 | 2051 | 1937 | 1428 | 7121 | 3668 | 2878 | 1639 | 2487.429
2029 | 2830 | 4058 | 6049 | 5422 | 2238 | 2952 | 7396 | 2079 | 1963 | 1447 | 7222 | 3716 | 2916 | 1669 | 2477.466
2030 | 2867 | 4067 | 6154 | 5514 | 2232 | 2933 | 7309 | 2108 | 1991 | 1466 | 7323 | 3766 | 2955 | 1699 | 2470.824
2031 | 2891 | 4076 | 6257 | 5604 | 2226 | 2925 | 7216 | 2139 | 2019 | 1487 | 7425 | 3819 | 2997 | 1729 | 2464.182
2032 | 2925 | 4083 | 6362 | 5696 | 2221 | 2917 | 7117 | 2169 | 2048 | 1507 | 7528 | 3872 | 3038 | 1761 | 2458.647
2033 | 2949 | 4122 | 6468 | 5789 | 2215 | 2910 | 7245 | 2202 | 2079 | 1530 | 7638 | 3930 | 3083 | 1792 | 2452.005
2034 | 2984 | 4162 | 6577 | 5884 | 2209 | 2902 | 7375 | 2234 | 2110 | 1552 | 7743 | 3986 | 3127 | 1825 | 2445.363
2035 | 3010 | 4202 | 6688 | 5981 | 2203 | 2894 | 7508 | 2270 | 2143 | 1577 | 7850 | 4050 | 3178 | 1857 | 2438.721
2036 | 3045 | 4242 | 6800 | 6079 | 2197 | 2887 | 7643 | 2304 | 2176 | 1601 | 7952 | 4112 | 3226 | 1891 | 2432.079
2037 | 3071 | 4282 | 6915 | 6179 | 2192 | 2879 | 7781 | 2342 | 2211 | 1627 | 8062 | 4179 | 3279 | 1925 | 2426.544
2038 | 3107 | 4322 | 7031 | 6281 | 2186 | 2872 | 7921 | 2379 | 2246 | 1653 | 8166 | 4246 | 3331 | 1959 | 2419.902
2039 | 3134 | 4363 | 7150 | 6385 | 2180 | 2864 | 8064 | 2419 | 2284 | 1681 | 8267 | 4317 | 3387 | 1995 | 2413.26
2040 | 3171 | 4403 | 7270 | 6490 | 2174 | 2856 | 8209 | 2455 | 2318 | 1706 | 8361 | 4382 | 3439 | 2031 | 2406.618
2041 | 3199 | 4443 | 7393 | 6598 | 2169 | 2849 | 8356 | 2499 | 2360 | 1737 | 8512 | 4461 | 3501 | 2067 | 2401.083
2042 | 3237 | 4484 | 7518 | 6707 | 2163 | 2841 | 8507 | 2544 | 2403 | 1768 | 8665 | 4542 | 3564 | 2104 | 2394.441
2043 | 3265 | 4528 | 7646 | 6818 | 2157 | 2834 | 8660 | 2590 | 2446 | 1800 | 8821 | 4623 | 3628 | 2142 | 2387.799
2044 | 3303 | 4573 | 7775 | 6931 | 2151 | 2827 | 8816 | 2637 | 2490 | 1832 | 8979 | 4707 | 3693 | 2181 | 2381.157
2045 | 3333 | 4617 | 7907 | 7046 | 2146 | 2819 | 8975 | 2684 | 2535 | 1865 | 9141 | 4791 | 3760 | 2220 | 2375.622
Black cells below are from "PSIP 2016 New Resource Assumptions UPDATED 11-MAR-16.xlsx" provided by Todd Kanja at HECO 2016-05-05
Size (MW) | 30 | 400 | 200 | 400 | 20 | DG-PV | 100 | 383 (3 x 1) | 152 (1 x 1) | 100 | 20 | 27 (3 x 9 MW) | 54 (6 x 9 MW) | 100 (6 x 16.8 MW) Power Barge
assumed | 30 | 400 | 200 | 400 | 20 | 0.005 | 100 | 383 | 152 | 100 | 20 | 27 | 54 | 100 | 20
Oahu 2016 Interconnect $ x 1000 | 13700 | Included in CapEx | Included in CapEx | Included in CapEx | $2,900 (46 kv) $13,700 (138 kv) |  | Included in CapEx | 30400 | 23300 | 16200 | Included in CapEx | 13700 | 15100 | 16200
assumed | 13700 | 0 | 0 | 0 | 8300 | 0 | 0 | 30400 | 23300 | 16200 | 0 | 13700 | 15100 | 16200 | 8300
| OnshoreWind | OffshoreWind | MauiOahuWind200 | MauiOahuWind400 | CentralFixedPV | DistPV | SolarCSPStorage | CC_383 | CC_152 | CT_100 | Biomass | IC_MCBH | IC_Schofield | IC_Barge | CentralTrackingPV
interconnect cost per kW | 456.6667 | 0 | 0 | 0 | 415 | 0 | 0 | 79.3734 | 153.2895 | 162 | 0 | 507.4074 | 279.6296 | 162 | 415
2016 Fixed O&M $/KW-Yr | 27.4 | 96.71 | 27.4 | 27.4 | 22.97 | NA | 92.38 | See CC OM Sheet | 17.29 | 9.01 | 79.05 | 34.46 | 34.46 | 34.46
2016 Variable O&M $/MWH | 0 | 0 | 0 | 0 | 0 | NA | 0 | See CC OM Sheet | 4.49 | 12.99 | 84.98 | 20.96 | 20.96 | 20.96
Fixed O&M | 27.4 | 96.71 | 27.4 | 27.4 | 22.97 | 0 | 92.38 | 17.29 | 17.29 | 9.01 | 79.05 | 34.46 | 34.46 | 34.46 | 22.97
Variable O&M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.49 | 4.49 | 12.99 | 84.98 | 20.96 | 20.96 | 20.96 | 0
Note on O6: Barge is used primarily for HECO, but could also serve as backup for JBPHH
Note on P8: See "tracking vs non-tracking PV costs.xlsx" and p. 40 of LBNL "Tracking the Sun VIII" at https://emp.lbl.gov/sites/all/files/lbnl-188238_2.pdf (Prices in 2014$.) Average ratio between cost of tracking and non-tracking systems in 2010-14 was 1.107. On the other hand, a dealer for ideematec quoted a total cost for their tracking structure and controls of $150-$250/kW, which is less than even a 10% markup. Before 2016-10-18, we used this approach (which doesn't account for future cost reductions with trackers): Average difference between tracking and non-tracking systems in 2010-14 was $0.362/Wdc (2014$). This is scaled down by 1.5 based on the DC/AC ratio used in the 2016-04-01 PSIP. This is scaled up by 1.405 to reflect the difference between Hawaii-specific costs and mainland costs, shown on p. F-4 of the 2016-04-01 PSIP. These adjustments give a total extra cost of $339 (2014$)/kW for tracking capability.

## storage
HAWAIIAN ELECTRIC COMPANY
2016 Power Supply Improvement Plan
Energy Storage Cost Assumptions
UPDATED MARCH 11, 2016
Application | Inertia | Contingency |  |  |  |  | Regulation / Renewable Smoothing |  |  |  |  | Load Shifting |  |  |  |  | Residential |  | Load Shifting Long Duration |  |  | Commercial |  | Grid Support
Size MW | 10 | 1 | 5 | 20 | 50 | 100 | 1 | 5 | 20 | 50 | 100 | 1 | 5 | 20 | 50 | 100 | 0.002 |  | 30 | 30 | 50 | 0.05 | 0.1 | 5
Technology | Flywheel | Lithium Ion | [14 empty] | LI / NO INVERTER | LI w/ Inverter and BoP | LI | PSH | PSH | LI | LI | LI
Duration Hours | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 4 | 4 | 4 | 4 | 4 | 4 |  | 6 | 6 | 6 | 2 | 2 | 2
Turnaround Efficiency | 85% | 81% |  |  |  |  | 81% |  |  |  |  | 88% |  |  |  |  | 88% |  |  | 80% | 80% | 88% | 88% | 81%
Discharge Cycles Per Year | 15000 | Up to 10 |  |  |  |  | Up to 15,000 |  |  |  |  | Up to 365 |  |  |  |  | Up to 365 |  | Up to 365 |  |  | Up to 365 |  | Up to 365
Depth of Discharge | 100% | Up to 100% |  |  |  |  | Up to 20% |  |  |  |  | Up to 100% |  |  |  |  | Up to 100% |  | Up to 100% |  |  | Up to 100% |  | Up to 100%
Plant Life Years | 15% | 15 |  |  |  |  | 15 |  |  |  |  | 15 |  |  |  |  | 10% |  | 15 | 40 | 40 | 10 | 10 | 15
Capital Cost in $/KILOWATT-HOUR (w/o Interconnection, w/o AFUDC)
Install Year | [16 empty] | Storage Only | Total System
2016 | 9400 | 1506 | 1506 | 1506 | 1506 | 1506 | 1083 | 1083 | 1083 | 1083 | 1083 | 660 | 660 | 660 | 660 | 660 | 506 | 1026 | 530 | 583 | 583 | 553 | 553 | 1083
2017 | 8632 | 1383 | 1383 | 1383 | 1383 | 1383 | 999 | 999 | 999 | 999 | 999 | 615 | 615 | 615 | 615 | 615 | 465 | 961 | 493 | 594 | 594 | 511 | 511 | 999
2018 | 7877 | 1262 | 1262 | 1262 | 1262 | 1262 | 914 | 914 | 914 | 914 | 914 | 565 | 565 | 565 | 565 | 565 | 416 | 884 | 454 | 605 | 605 | 461 | 461 | 914
2019 | 7253 | 1162 | 1162 | 1162 | 1162 | 1162 | 843 | 843 | 843 | 843 | 843 | 524 | 524 | 524 | 524 | 524 | 373 | 817 | 421 | 615 | 615 | 417 | 417 | 843
2020 | 6729 | 1078 | 1078 | 1078 | 1078 | 1078 | 782 | 782 | 782 | 782 | 782 | 487 | 487 | 487 | 487 | 487 | 335 | 757 | 391 | 626 | 626 | 378 | 378 | 782
2021 | 6317 | 1012 | 1012 | 1012 | 1012 | 1012 | 737 | 737 | 737 | 737 | 737 | 461 | 461 | 461 | 461 | 461 | 317 | 729 | 371 | 638 | 638 | 359 | 359 | 737
2022 | 5972 | 957 | 957 | 957 | 957 | 957 | 698 | 698 | 698 | 698 | 698 | 440 | 440 | 440 | 440 | 440 | 303 | 706 | 353 | 649 | 649 | 342 | 342 | 698
2023 | 5678 | 910 | 910 | 910 | 910 | 910 | 666 | 666 | 666 | 666 | 666 | 422 | 422 | 422 | 422 | 422 | 290 | 687 | 339 | 661 | 661 | 328 | 328 | 666
2024 | 5429 | 870 | 870 | 870 | 870 | 870 | 638 | 638 | 638 | 638 | 638 | 406 | 406 | 406 | 406 | 406 | 280 | 670 | 326 | 673 | 673 | 316 | 316 | 638
2025 | 5214 | 835 | 835 | 835 | 835 | 835 | 614 | 614 | 614 | 614 | 614 | 393 | 393 | 393 | 393 | 393 | 270 | 655 | 316 | 685 | 685 | 305 | 305 | 614
2026 | 5029 | 806 | 806 | 806 | 806 | 806 | 594 | 594 | 594 | 594 | 594 | 382 | 382 | 382 | 382 | 382 | 262 | 643 | 306 | 697 | 697 | 296 | 296 | 594
2027 | 4869 | 780 | 780 | 780 | 780 | 780 | 576 | 576 | 576 | 576 | 576 | 372 | 372 | 372 | 372 | 372 | 256 | 632 | 298 | 710 | 710 | 289 | 289 | 576
2028 | 4730 | 758 | 758 | 758 | 758 | 758 | 560 | 560 | 560 | 560 | 560 | 363 | 363 | 363 | 363 | 363 | 250 | 623 | 291 | 723 | 723 | 282 | 282 | 560
2029 | 4609 | 738 | 738 | 738 | 738 | 738 | 547 | 547 | 547 | 547 | 547 | 355 | 355 | 355 | 355 | 355 | 245 | 615 | 285 | 736 | 736 | 276 | 276 | 547
2030 | 4503 | 721 | 721 | 721 | 721 | 721 | 535 | 535 | 535 | 535 | 535 | 349 | 349 | 349 | 349 | 349 | 240 | 608 | 280 | 749 | 749 | 271 | 271 | 535
2031 | 4409 | 706 | 706 | 706 | 706 | 706 | 525 | 525 | 525 | 525 | 525 | 343 | 343 | 343 | 343 | 343 | 236 | 601 | 275 | 762 | 762 | 267 | 267 | 525
2032 | 4327 | 693 | 693 | 693 | 693 | 693 | 516 | 516 | 516 | 516 | 516 | 338 | 338 | 338 | 338 | 338 | 232 | 596 | 271 | 776 | 776 | 263 | 263 | 516
2033 | 4255 | 682 | 682 | 682 | 682 | 682 | 508 | 508 | 508 | 508 | 508 | 333 | 333 | 333 | 333 | 333 | 229 | 591 | 268 | 790 | 790 | 259 | 259 | 508
2034 | 4190 | 671 | 671 | 671 | 671 | 671 | 500 | 500 | 500 | 500 | 500 | 329 | 329 | 329 | 329 | 329 | 227 | 587 | 264 | 804 | 804 | 256 | 256 | 500
2035 | 4133 | 662 | 662 | 662 | 662 | 662 | 494 | 494 | 494 | 494 | 494 | 326 | 326 | 326 | 326 | 326 | 224 | 583 | 262 | 819 | 819 | 253 | 253 | 494
2036 | 4083 | 654 | 654 | 654 | 654 | 654 | 488 | 488 | 488 | 488 | 488 | 323 | 323 | 323 | 323 | 323 | 222 | 579 | 259 | 833 | 833 | 251 | 251 | 488
2037 | 4038 | 647 | 647 | 647 | 647 | 647 | 483 | 483 | 483 | 483 | 483 | 320 | 320 | 320 | 320 | 320 | 220 | 576 | 257 | 848 | 848 | 249 | 249 | 483
2038 | 3998 | 641 | 641 | 641 | 641 | 641 | 479 | 479 | 479 | 479 | 479 | 317 | 317 | 317 | 317 | 317 | 218 | 574 | 255 | 864 | 864 | 247 | 247 | 479
2039 | 3962 | 635 | 635 | 635 | 635 | 635 | 475 | 475 | 475 | 475 | 475 | 315 | 315 | 315 | 315 | 315 | 217 | 571 | 253 | 879 | 879 | 245 | 245 | 475
2040 | 3930 | 630 | 630 | 630 | 630 | 630 | 471 | 471 | 471 | 471 | 471 | 313 | 313 | 313 | 313 | 313 | 216 | 569 | 252 | 895 | 895 | 243 | 243 | 471
2041 | 3902 | 625 | 625 | 625 | 625 | 625 | 468 | 468 | 468 | 468 | 468 | 312 | 312 | 312 | 312 | 312 | 214 | 567 | 250 | 911 | 911 | 242 | 242 | 468
2042 | 3876 | 621 | 621 | 621 | 621 | 621 | 465 | 465 | 465 | 465 | 465 | 310 | 310 | 310 | 310 | 310 | 213 | 565 | 249 | 928 | 928 | 241 | 241 | 465
2043 | 3854 | 617 | 617 | 617 | 617 | 617 | 463 | 463 | 463 | 463 | 463 | 309 | 309 | 309 | 309 | 309 | 212 | 564 | 248 | 944 | 944 | 240 | 240 | 463
2044 | 3833 | 614 | 614 | 614 | 614 | 614 | 461 | 461 | 461 | 461 | 461 | 307 | 307 | 307 | 307 | 307 | 211 | 563 | 247 | 961 | 961 | 239 | 239 | 461
2045 | 3815 | 611 | 611 | 611 | 611 | 611 | 459 | 459 | 459 | 459 | 459 | 306 | 306 | 306 | 306 | 306 | 211 | 561 | 246 | 979 | 979 | 238 | 238 | 459
Capital Cost in $/KILOWATT (w/o Interconnection, w/o AFUDC)
Install Year
2016 | 2350 | 753 | 753 | 753 | 753 | 753 | 1083 | 1083 | 1083 | 1083 | 1083 | 2640 | 2640 | 2640 | 2640 | 2640 | 2023 | 4103 | 3180 | 3500 | 3500 | 1106 | 1106 | 2166
2017 | 2158 | 692 | 692 | 692 | 692 | 692 | 999 | 999 | 999 | 999 | 999 | 2458 | 2458 | 2458 | 2458 | 2458 | 1858 | 3844 | 2960 | 3563 | 3563 | 1021 | 1021 | 1998
2018 | 1969 | 631 | 631 | 631 | 631 | 631 | 914 | 914 | 914 | 914 | 914 | 2261 | 2261 | 2261 | 2261 | 2261 | 1663 | 3536 | 2723 | 3627 | 3627 | 922 | 922 | 1827
2019 | 1813 | 581 | 581 | 581 | 581 | 581 | 843 | 843 | 843 | 843 | 843 | 2095 | 2095 | 2095 | 2095 | 2095 | 1492 | 3267 | 2523 | 3692 | 3692 | 834 | 834 | 1686
2020 | 1682 | 539 | 539 | 539 | 539 | 539 | 782 | 782 | 782 | 782 | 782 | 1948 | 1948 | 1948 | 1948 | 1948 | 1340 | 3028 | 2346 | 3759 | 3759 | 757 | 757 | 1565
2021 | 1579 | 506 | 506 | 506 | 506 | 506 | 737 | 737 | 737 | 737 | 737 | 1846 | 1846 | 1846 | 1846 | 1846 | 1270 | 2918 | 2223 | 3827 | 3827 | 717 | 717 | 1474
2022 | 1493 | 478 | 478 | 478 | 478 | 478 | 698 | 698 | 698 | 698 | 698 | 1760 | 1760 | 1760 | 1760 | 1760 | 1211 | 2825 | 2120 | 3895 | 3895 | 684 | 684 | 1397
2023 | 1420 | 455 | 455 | 455 | 455 | 455 | 666 | 666 | 666 | 666 | 666 | 1687 | 1687 | 1687 | 1687 | 1687 | 1161 | 2746 | 2032 | 3966 | 3966 | 656 | 656 | 1332
2024 | 1357 | 435 | 435 | 435 | 435 | 435 | 638 | 638 | 638 | 638 | 638 | 1625 | 1625 | 1625 | 1625 | 1625 | 1118 | 2679 | 1957 | 4037 | 4037 | 631 | 631 | 1276
2025 | 1304 | 418 | 418 | 418 | 418 | 418 | 614 | 614 | 614 | 614 | 614 | 1572 | 1572 | 1572 | 1572 | 1572 | 1081 | 2621 | 1893 | 4110 | 4110 | 611 | 611 | 1228
2026 | 1257 | 403 | 403 | 403 | 403 | 403 | 594 | 594 | 594 | 594 | 594 | 1526 | 1526 | 1526 | 1526 | 1526 | 1050 | 2572 | 1838 | 4184 | 4184 | 593 | 593 | 1187
2027 | 1217 | 390 | 390 | 390 | 390 | 390 | 576 | 576 | 576 | 576 | 576 | 1486 | 1486 | 1486 | 1486 | 1486 | 1023 | 2529 | 1790 | 4259 | 4259 | 577 | 577 | 1152
2028 | 1183 | 379 | 379 | 379 | 379 | 379 | 560 | 560 | 560 | 560 | 560 | 1452 | 1452 | 1452 | 1452 | 1452 | 999 | 2491 | 1748 | 4336 | 4336 | 564 | 564 | 1121
2029 | 1152 | 369 | 369 | 369 | 369 | 369 | 547 | 547 | 547 | 547 | 547 | 1422 | 1422 | 1422 | 1422 | 1422 | 978 | 2459 | 1712 | 4414 | 4414 | 552 | 552 | 1094
2030 | 1126 | 361 | 361 | 361 | 361 | 361 | 535 | 535 | 535 | 535 | 535 | 1395 | 1395 | 1395 | 1395 | 1395 | 960 | 2430 | 1680 | 4493 | 4493 | 542 | 542 | 1070
2031 | 1102 | 353 | 353 | 353 | 353 | 353 | 525 | 525 | 525 | 525 | 525 | 1372 | 1372 | 1372 | 1372 | 1372 | 944 | 2405 | 1652 | 4574 | 4574 | 533 | 533 | 1049
2032 | 1082 | 347 | 347 | 347 | 347 | 347 | 516 | 516 | 516 | 516 | 516 | 1352 | 1352 | 1352 | 1352 | 1352 | 930 | 2383 | 1628 | 4656 | 4656 | 525 | 525 | 1031
2033 | 1064 | 341 | 341 | 341 | 341 | 341 | 508 | 508 | 508 | 508 | 508 | 1334 | 1334 | 1334 | 1334 | 1334 | 917 | 2363 | 1606 | 4740 | 4740 | 518 | 518 | 1015
2034 | 1048 | 336 | 336 | 336 | 336 | 336 | 500 | 500 | 500 | 500 | 500 | 1318 | 1318 | 1318 | 1318 | 1318 | 907 | 2346 | 1587 | 4825 | 4825 | 512 | 512 | 1001
2035 | 1033 | 331 | 331 | 331 | 331 | 331 | 494 | 494 | 494 | 494 | 494 | 1304 | 1304 | 1304 | 1304 | 1304 | 897 | 2331 | 1570 | 4912 | 4912 | 506 | 506 | 988
2036 | 1021 | 327 | 327 | 327 | 327 | 327 | 488 | 488 | 488 | 488 | 488 | 1291 | 1291 | 1291 | 1291 | 1291 | 888 | 2317 | 1555 | 5001 | 5001 | 502 | 502 | 977
2037 | 1009 | 323 | 323 | 323 | 323 | 323 | 483 | 483 | 483 | 483 | 483 | 1280 | 1280 | 1280 | 1280 | 1280 | 881 | 2305 | 1541 | 5091 | 5091 | 497 | 497 | 967
2038 | 999 | 320 | 320 | 320 | 320 | 320 | 479 | 479 | 479 | 479 | 479 | 1270 | 1270 | 1270 | 1270 | 1270 | 874 | 2295 | 1529 | 5182 | 5182 | 493 | 493 | 958
2039 | 991 | 317 | 317 | 317 | 317 | 317 | 475 | 475 | 475 | 475 | 475 | 1261 | 1261 | 1261 | 1261 | 1261 | 868 | 2285 | 1519 | 5276 | 5276 | 490 | 490 | 950
2040 | 983 | 315 | 315 | 315 | 315 | 315 | 471 | 471 | 471 | 471 | 471 | 1253 | 1253 | 1253 | 1253 | 1253 | 862 | 2276 | 1509 | 5370 | 5370 | 487 | 487 | 943
2041 | 975 | 313 | 313 | 313 | 313 | 313 | 468 | 468 | 468 | 468 | 468 | 1246 | 1246 | 1246 | 1246 | 1246 | 857 | 2269 | 1501 | 5467 | 5467 | 484 | 484 | 937
2042 | 969 | 311 | 311 | 311 | 311 | 311 | 465 | 465 | 465 | 465 | 465 | 1240 | 1240 | 1240 | 1240 | 1240 | 853 | 2262 | 1493 | 5566 | 5566 | 482 | 482 | 931
2043 | 963 | 309 | 309 | 309 | 309 | 309 | 463 | 463 | 463 | 463 | 463 | 1234 | 1234 | 1234 | 1234 | 1234 | 849 | 2256 | 1486 | 5666 | 5666 | 479 | 479 | 926
2044 | 958 | 307 | 307 | 307 | 307 | 307 | 461 | 461 | 461 | 461 | 461 | 1229 | 1229 | 1229 | 1229 | 1229 | 846 | 2250 | 1480 | 5768 | 5768 | 478 | 478 | 921
2045 | 954 | 306 | 306 | 306 | 306 | 306 | 459 | 459 | 459 | 459 | 459 | 1224 | 1224 | 1224 | 1224 | 1224 | 842 | 2245 | 1475 | 5872 | 5872 | 476 | 476 | 917
Enegy Storage Construction S-Curve
Construction Year
-6 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NA | NA | 0% | 5% | 5% | NA | NA | 0%
-5 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NA | NA | 0% | 10% | 10% | NA | NA | 0%
-4 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NA | NA | 0% | 10% | 10% | NA | NA | 0%
-3 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NA | NA | 0% | 20% | 20% | NA | NA | 0%
-2 | 20% | 0% | 0% | 20% | 20% | 20% | 0% | 0% | 20% | 20% | 20% | 0% | 0% | 20% | 20% | 30% | NA | NA | 30% | 30% | 30% | NA | NA | 0%
-1 | 80% | 100% | 100% | 80% | 80% | 80% | 100% | 100% | 80% | 80% | 80% | 100% | 100% | 80% | 80% | 70% | NA | NA | 70% | 25% | 25% | NA | NA | 100%
COD
| 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 100%
AFUDC Adder based on S-Curve | 4.024% | 2.461% | 2.461% | 4.024% | 4.024% | 4.024% | 2.461% | 2.461% | 4.024% | 4.024% | 4.024% | 2.461% | 2.461% | 4.024% | 4.024% | 4.806% | NA | NA | 4.81% | 16.36% | 16.36% | NA | NA | 2.46%
Enegy Storage Interconnection and O&M Costs
Oahu Interconnection Cost 2016 $x1000 | 2700 | NA | 2700 | $2,700 46 KV / $13,100 138 KV | 14200 | 15300 | NA | 2700 | $2,700 46 KV / $13,100 138 KV | 14200 | 15300 | NA | 2700 | $2,700 46 KV $13,100 138 KV | 14200 | 15300 | NA | NA | 13100 | 13100 | 14200 | NA | NA | 2700
Escalator | 1.8% | NA | 1.8% | 1.8% | 1.8% | 1.8% | NA | 1.8% | 1.8% | 1.8% | 1.8% | NA | 1.8% | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | 1.8%
Maui Interconnection Costs $2016 $x1000 | 7500 | 2000 | 7500 | 6000 | NA | NA | 2000 | 7500 | 6000 | NA | NA | 2000 | 7500 | 5500 | NA | NA | NA | NA | 6000 | 6000 | NA | NA | NA | 7500
Escalator | 1.8% | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | NA | NA | 1.8% | 1.8% | NA | NA | NA | 1.8%
Hawaii Interconnection Costs 2016 $x1000 | 3000 | 200 | 2120 | 5500 | NA | NA | 200 | 2120 | 5500 | NA | NA | 200 | 2120 | 5500 | NA | NA | NA | NA | 5500 | 5500 | NA | NA | NA | 2120
Escalator | 1.8% | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | NA | NA | 1.8% | 1.8% | NA | NA | NA | 1.8%
Fixed O&M 2016 $/KW-Yr |  | 89.08 | 21.26 | 8.95 | 6.37 | 5.42 | 91.41 | 23.58 | 11.27 | 8.7 | 7.61 | 103.12 | 35.3 | 22.99 | 20.41 | 19.47 | NA | NA | 27.49 | 30 | 30 | NA | NA | 28.81
Escalator | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | 1.8%
Changes and modifications
| 2016-02-29 | HDB | Updated interconnection costs for Oahu to reflect removal of land costs from substation cost estimate (assumes BESS project includes land.
| 2016-03-11 | HDB | Updated BESS + inverter cost for residential energy storage to reflect changes received from BCG.
| 2016-03-11 | HDB | Added row for AFUDC factors being used by planning teams

## sales
load_zone | year | underlying forecast (GWh) | energy efficiency (GWh) | underlying forecast (MW) | energy efficiency (MW)
Oahu | 2016 | 8286 | -1076.9 | 1363.7 | -198.7
Oahu | 2017 | 8481.3 | -1149 | 1397.7 | -215.7
Oahu | 2018 | 8691.4 | -1223.6 | 1431.7 | -232.7
Oahu | 2019 | 8816.8 | -1287.8 | 1447.7 | -248.7
Oahu | 2020 | 8885.6 | -1375.1 | 1454.7 | -266.7
Oahu | 2021 | 8933.4 | -1465.8 | 1465.7 | -284.7
Oahu | 2022 | 8952.7 | -1556.6 | 1468.7 | -302.7
Oahu | 2023 | 8987 | -1647.4 | 1473.7 | -321.7
Oahu | 2024 | 9053.7 | -1744.1 | 1479.7 | -344.7
Oahu | 2025 | 9087.4 | -1846 | 1488.7 | -369.7
Oahu | 2026 | 9154 | -1957 | 1499.7 | -400.7
Oahu | 2027 | 9229.7 | -2079.5 | 1511.7 | -436.7
Oahu | 2028 | 9329.1 | -2209.1 | 1524.7 | -474.7
Oahu | 2029 | 9376.6 | -2345.6 | 1547.7 | -560.7
Oahu | 2030 | 9459.9 | -2486 | 1555.7 | -568.7
Oahu | 2031 | 9513.1 | -2552.8 | 1563.7 | -570.7
Oahu | 2032 | 9581.3 | -2561.4 | 1570.7 | -571.7
Oahu | 2033 | 9604.9 | -2567.8 | 1578.7 | -573.7
Oahu | 2034 | 9651.7 | -2573.6 | 1586.7 | -576.7
Oahu | 2035 | 9703.5 | -2584.1 | 1595.7 | -581.7
Oahu | 2036 | 9785.3 | -2600.8 | 1605.7 | -583.7
Oahu | 2037 | 9823.4 | -2615.4 | 1615.7 | -587.7
Oahu | 2038 | 9885.8 | -2628.1 | 1625.7 | -591.7
Oahu | 2039 | 9947.4 | -2644.4 | 1634.7 | -596.7
Oahu | 2040 | 10031.6 | -2664.9 | 1643.7 | -599.7
Oahu | 2041 | 10065.8 | -2680.1 | 1651.7 | -602.7
Oahu | 2042 | 10122.3 | -2691.8 | 1660.7 | -606.7
Oahu | 2043 | 10178 | -2707.1 | 1670.7 | -611.7
Oahu | 2044 | 10256.7 | -2726.4 | 1679.7 | -614.7
Oahu | 2045 | 10287.7 | -2741.4 | 1534.7 | -516.7
Note on C1: from 2016-04-01 PSIP Book 1, p. J-44
Note on D1: from 2016-04-01 PSIP Book 1, p. J-44
Note on E1: from 2016-04-01 PSIP Book 1, p. J-49
Note on F1: from 2016-04-01 PSIP Book 1, p. J-49

## DistPV
year | dist PV total | year | addition | tuple
2016 | 443.9935 | 2016 | 443.9935 | (2016, 'DistPV', 443.993468266547),
2017.0012 | 536.7452 | 2017 | 92.7518 | (2017, 'DistPV', 92.751756737742),
2018.0342 | 564.0235 | 2018 | 27.2782 | (2018, 'DistPV', 27.278236032368),
2019.0195 | 590.2116 | 2019 | 26.1881 | (2019, 'DistPV', 26.188129564885),
2019.9889 | 612.0361 | 2020 | 21.8245 | (2020, 'DistPV', 21.8245069017911),
2021.0061 | 627.3104 | 2021 | 15.2743 | (2021, 'DistPV', 15.27427771741),
2022.0232 | 639.3143 | 2022 | 12.004 | (2022, 'DistPV', 12.0039583149589),
2023.0085 | 650.225 | 2023 | 10.9107 | (2023, 'DistPV', 10.910655054315),
2024.0097 | 661.1388 | 2024 | 10.9139 | (2024, 'DistPV', 10.913851847475),
2024.995 | 672.0495 | 2025 | 10.9107 | (2025, 'DistPV', 10.910655054316),
2025.9962 | 681.87 | 2026 | 9.8205 | (2026, 'DistPV', 9.82054858683205),
2027.0133 | 692.7807 | 2027 | 10.9107 | (2027, 'DistPV', 10.910655054316),
2028.0145 | 703.6914 | 2028 | 10.9107 | (2028, 'DistPV', 10.910655054315),
2028.9999 | 717.8787 | 2029 | 14.1874 | (2029, 'DistPV', 14.1873680430859),
2030.017 | 727.6993 | 2030 | 9.8205 | (2030, 'DistPV', 9.82054858683205),
2031.0183 | 738.6131 | 2031 | 10.9139 | (2031, 'DistPV', 10.913851847475),
2032.0036 | 748.4337 | 2032 | 9.8205 | (2032, 'DistPV', 9.82054858683193),
2032.9889 | 762.6178 | 2033 | 14.1842 | (2033, 'DistPV', 14.1841712499261),
2034.006 | 770.2582 | 2034 | 7.6403 | (2034, 'DistPV', 7.64033565186492),
2034.9755 | 783.3522 | 2035 | 13.0941 | (2035, 'DistPV', 13.094064782442),
2036.0084 | 793.1728 | 2036 | 9.8205 | (2036, 'DistPV', 9.82054858683205),
2037.0095 | 804.093 | 2037 | 10.9202 | (2037, 'DistPV', 10.9202454337949),
2037.9949 | 813.7629 | 2038 | 9.6699 | (2038, 'DistPV', 9.66989970917803),
2039.0369 | 825.9143 | 2039 | 12.1514 | (2039, 'DistPV', 12.1514103994531),
2039.9974 | 838.1541 | 2040 | 12.2397 | (2040, 'DistPV', 12.2397218104919),
2040.9986 | 849.9215 | 2041 | 11.7674 | (2041, 'DistPV', 11.7673956211361),
2042.0156 | 860.8321 | 2042 | 10.9107 | (2042, 'DistPV', 10.9106550543149),
2043.0328 | 870.6527 | 2043 | 9.8205 | (2043, 'DistPV', 9.82054858683205),
2044.034 | 885.9301 | 2044 | 15.2775 | (2044, 'DistPV', 15.27747451057),
2045 | 896.2218 | 2045 | 10.2917 | (2045, 'DistPV', 10.291675978754),